#### ULTRA OIL BOILER-Series 3

##### SUGGESTED SPECIFICATIONS

- General Requirements

  - Furnish and install 		 (qty) chimney vent, or direct vent, cast iron, 3-pass design, sectional, water boiler(s).

  - Install boiler unit(s) in compliance with manufacturer’s installation instructions.
All work must be done in a neat and workmanlike manner.

  - Weil-McLain 		 (qty) UO - 		 (size) boiler(s) capable of burning No. 2 fuel oil.

  - Boiler assembly:

    - Boiler(s) to be factory packaged, wired, and tested with jacket, circulator, burner, and controls. Boiler(s) shall be shipped ready for field installation.

  - Boiler(s) shall be 87.0% minimum efficient as rated by D.O.E. seasonal efficiency (AFUE) and listed in the current AHRI Directory of Certified Ratings.

  - Boiler(s) shall meet U.S. Environmental Protection Agency and Department of Energy guidelines for “ENERGY STAR” energy efficiency.

  - Boiler(s) shall have AHRI gross output(s) at 100% firing rate 		 MBH per boiler.

  - Boiler(s) shall be manufactured to conform to Section IV of the ASME Boiler and Pressure Vessel Code.

    - Individual sections and section assembly shall undergo hydrostatic pressure test at factory in accordance with ASME requirements for 50 PSIG working pressure and cast as part of section with ASME symbol.

    - Water boiler(s) maximum allowable working pressure will be 50 PSIG.

  - Regulatory requirements:

    - Boiler(s) and controls shall comply with applicable regulations.

  - Submittals

    - Submit shop drawings and product data.

    - Submittal packet to include boiler descriptive literature, installation instructions, operating instructions, and maintenance instructions.

- Product

  - Acceptable boiler manufacturer(s) include(s):

    - Weil-McLain only, as specified in Part 1, Paragraph C.

    - Other manufacturer or other Weil-McLain boiler(s) must comply with specifying engineer’s requirements, including:

      - Full intent of these specifications, and

      - Provide complete submittal including literature, wiring diagrams, fuel piping diagrams, and a list of similar installations.

      - Submittals to be presented to specifying engineer at least seven working days for approval before bid opening. Substitutions are not permitted after contract is awarded.

  - Boiler construction

    - Boiler sections

      - Factory assembled in one block with tie rods and sealed with high temperature silicone coated fiberglass rope between sections to assure a permanent gas-tight seal.

      - Sealed watertight by elastomer sealing rings, not cast iron nipples. Each port opening shall be machined to completely capture sealing ring between sections in order to assure uniform compression of the sealing rings and to protect the sealing rings from contaminants.

      - Provided with sufficient tappings to install required controls.

      - Provided with a reversible swing-away burner mounting door to allow greater ease of service.

      - Provided with the means to vent out the rear of the boiler.

      - Shipped with heavy gauge steel jacket(s) with durable powdered paint enamel finish. Jacket designed to be installed after connecting supply and return piping.

  - Boiler foundation(s)

    - Installer shall construct required level concrete foundation(s) and support(s) where boiler room floor is uneven or will not support the weight of the boiler(s).

  - Boiler trim

    - All electrical components to be of high quality and third (3rd) party recognized.

    - Electrical wiring to be factory installed utilizing a labeled terminal strip to help assure correct wiring.

    - Water boiler(s) standard controls furnished:

      - Electronic Aquastat control with circulator relay and LWCO functionality.

      - Combination pressure-temperature gauge. Dial clearly marked and easy to read.

      - A.S.M.E. certified pressure relief valve, set to relieve at 30 PSIG. Side outlet discharge type; installer to pipe outlet to floor drain or near floor.

## Additional Components

## Optional Components

- 50 psi relief valve

- Advanced Features Module (AFM)

  - Outdoor reset

  - Low temperature mixing

  - Setpoint operation

  - DHW priority

  - DHW priority override

  - DHW post purge

  - Stage fire two boilers

  - Automatic boiler differential

  - Boiler protection

  - Warm weather shutdown

  - Freeze protection

  - Mixing device exercise

  - Pump exercise

  - Test sequence

  - LCD remote display

  - Run hours log

  - Plug-in terminals

## Boiler Manuals

    - The boiler(s) shall be provided with complete instruction manuals, including:

      - Boiler Installation Manual

      - User’s Manual

C-822(699)