#### PEG SERIES BOILER

SUGGESTED SPECIFICATIONS

I.	General Requirements

  - Furnish and install 		 (qty) low pressure, natural draft, cast iron sectional boiler(s).

  - Install boiler unit(s) in compliance with manufacturer’s installation instructions.
All work must be done in a neat and workmanlike manner.

  - Weil-McLain 		 (qty) PEG - 		 (size) ( ) PIDN packaged boiler(s) capable of burning natural gas between 5” to 13” w.c. inlet pressure.

  - Boiler(s) to be steam.

  - Boiler(s) shall be 82.8% minimum efficient as rated by D.O.E. seasonal efficiency (AFUE) and listed in the current AHRI Directory of Certified Ratings.

  - Boiler(s) shall have an AHRI gross output(s) at 100% firing rate 		 MBH per boiler.

  - Boiler(s) to be factory packaged, wired, and fire tested and shall be shipped ready for field installation.

  - Boiler(s) shall be manufactured to conform to Section IV of the ASME Boiler and Pressure Vessel Code.

    - Individual sections and section assembly shall undergo hydrostatic pressure test at factory in accordance with ASME requirements.

    - Maximum allowable working pressure 15 PSIG steam and cast as part of section with ASME symbol.

  - Regulatory requirements:

    - Boiler(s) and controls shall comply with applicable regulations.

  - Submittals

    - Submit shop drawings and product data.

    - Submittal packet to include boiler descriptive literature, installation instructions, operating instructions, and maintenance instructions.

- Product

  - Acceptable boiler manufacturer(s) include(s):

    - Weil-McLain only, as specified in Part 1, Paragraph C.

    - Other manufacturer or other Weil-McLain boiler(s) must comply with specifying engineer’s requirements, including:

      - Full intent of these specifications, and

      - Provide complete submittal including literature, wiring diagrams, fuel piping diagrams, and a list of similar installations.

      - Submittals to be presented to specifying engineer at least seven working days for approval before bid opening. Substitutions are not permitted after contract is awarded.

  - Boiler construction

    - Boiler sections

      - Factory assembled in one block with tie rods and sealed with high temperature sealant to assure a permanent gas-tight seal.

      - Sealed watertight by elastomer sealing rings, not cast iron nipples. Each port opening shall be machined to completely capture sealing ring between sections in order to assure uniform compression of the sealing rings and to protect the sealing rings from contaminants.

      - Provided with sufficient tappings to install required controls.

    - Boiler(s)

      - Designed with a low silhouette and horizontal draft hood to provide maximum headroom.

      - Provided with an automatic vent damper to prevent heat from escaping up the chimney during off-cycle.

      - Shipped with insulated heavy gauge steel jacket(s) with durable powdered paint enamel finish. Jacket designed to be installed after connecting supply and return piping.

  - Boiler foundation(s)

    - Installer shall construct required level concrete foundation(s) and support(s) where boiler room floor is uneven or will not support the weight of the boiler(s).

  - Boiler trim

    - All electrical components to be of high quality and bear the UL label.

    - Electrical wiring to utilize a labeled and color-coded wiring harness to help assure correct wiring.

    - Steam boiler(s) standard controls furnished:

      - High pressure limit control. (15 PSI maximum allowable steam pressure)

      - Steam pressure gauge. Dial clearly marked and easy to read.

      - A.S.M.E. certified pressure relief valve, set to relieve at 15 PSIG. Side outlet discharge type; installer to pipe outlet to floor drain or near floor.

      - Low water cut-off (LWCO). LWCO shall be ( ) electrode or ( ) float-mechanism (check one) type capable of shutting down the boiler in event of a low water situation.

      - Transformer rated for 40VA.

## Boiler Manuals

    - The boiler(s) shall be provided with complete instruction manuals, including:

      - Boiler Installation Manual

      - Gas Control Supplement

      - User’s Information Manual